## WTG Yield Wake
WTG 1
Diameter |  | 280 | m
Swept area |  | 61575.216 | m^2
Rated power |  | 20 | MW
Power density rotor |  | 324.806 | W/m^2
Rated rotor speed |  | 7 | rpm
Rated tip speed |  | 102.6254 | m/s
Hub height |  | 160 | m
# of WTGs:
WTG 1 Parameters*) |  |  |  |  | Offshore Site 1 |  |  | 80
Wind speed | Power in the Wind | WTG Power | C_P | C_T | Free windspeed at hub height | Time | Gross Yield | Park Efficiency | Gross Yield incl. Wake Loss
(m/s) | (MW) | (MW) |  |  | (m/s) | % of year | (MWh/year) | % | (MWh/year)
0.5 | 0.0047105 | 0 | 0 | 0 | 0.5 | 0.652 | 0
1.5 | 0.12718 | 0 | 0 | 0 | 1.5 | 1.735 | 0
2.5 | 0.58881 | 0 | 0 | 0 | 2.5 | 3.356 | 0
3.5 | 1.6157 | 0.437 | 0.27047 | 0.855 | 3.5 | 4.832 | 185.1015 | 48.94% | 7246.525
4.5 | 3.434 | 1.423 | 0.41439 | 0.855 | 4.5 | 6.39 | 797.0898 | 56.66% | 36132.9691
5.5 | 6.2697 | 2.83 | 0.45138 | 0.855 | 5.5 | 7.657 | 1899.5317 | 61.63% | 93659.2279
6.5 | 10.349 | 4.772 | 0.46111 | 0.858 | 6.5 | 8.732 | 3652.7137 | 63.67% | 186041.2062
7.5 | 15.898 | 7.46 | 0.46924 | 0.863 | 7.5 | 9.448 | 6178.4591 | 64.58% | 319182.8734
8.5 | 23.1427 | 10.949 | 0.47311 | 0.84 | 8.5 | 9.619 | 9232.2137 | 66.2% | 488953.4761
9.5 | 32.3093 | 14.623 | 0.45259 | 0.752 | 9.5 | 9.123 | 11694.3374 | 69.86% | 653553.437
10.5 | 43.624 | 17.73 | 0.40643 | 0.641 | 10.5 | 8.192 | 12732.1031 | 75.62% | 770256.4134
11.5 | 57.3127 | 19.442 | 0.33923 | 0.521 | 11.5 | 7.082 | 12069.7515 | 83.77% | 808849.1604
12.5 | 73.6016 | 19.921 | 0.27066 | 0.402 | 12.5 | 5.825 | 10172.0511 | 91.79% | 746939.7361
13.5 | 92.7169 | 19.991 | 0.21561 | 0.309 | 13.5 | 4.558 | 7987.4896 | 96.66% | 617663.6709
14.5 | 114.8845 | 20 | 0.17409 | 0.244 | 14.5 | 3.373 | 5913.5436 | 99.18% | 469192.0147
15.5 | 140.3306 | 20 | 0.14252 | 0.197 | 15.5 | 2.414 | 4232.2248 | 99.94% | 338385.1175
16.5 | 169.2814 | 20 | 0.11815 | 0.162 | 16.5 | 1.801 | 3157.5132 | 99.94% | 252457.1651
17.5 | 201.9629 | 20 | 0.099028 | 0.136 | 17.5 | 1.415 | 2480.778 | 99.94% | 198349.1886
18.5 | 238.6012 | 20 | 0.083822 | 0.116 | 18.5 | 1.146 | 2009.1672 | 99.94% | 160641.8164
19.5 | 279.4224 | 20 | 0.071576 | 0.1 | 19.5 | 0.864 | 1514.7648 | 99.94% | 121112.1547
20.5 | 324.6526 | 20 | 0.061604 | 0.088 | 20.5 | 0.612 | 1072.9584 | 99.94% | 85787.7763
21.5 | 374.518 | 20 | 0.053402 | 0.078 | 21.5 | 0.435 | 762.642 | 99.94% | 60976.6057
22.5 | 429.2447 | 20 | 0.046593 | 0.07 | 22.5 | 0.294 | 515.4408 | 99.94% | 41211.7749
23.5 | 489.0587 | 18.4 | 0.037623 | 0.058 | 23.5 | 0.181 | 291.9429 | 104% | 24289.6463
24.5 | 554.1861 | 15.2 | 0.027428 | 0.044 | 24.5 | 0.109 | 145.2351 | 104% | 12083.5593
25.5 | 624.8531 | 12 | 0.019205 | 0.033 | 25.5 | 0.071 | 74.6863 | 104% | 6213.9018
26.5 | 701.2857 | 8.8 | 0.012548 | 0.023 | 26.5 | 0.039 | 30.0849 | 104% | 2503.0647
27.5 | 783.7101 | 5.6 | 0.0071455 | 0.0015 | 27.5 | 0.027 | 13.2542 | 104% | 1102.7488
28.5 | 872.3524 | 0 | 0 | 0 | 28.5 | 0.018 | 0 | 0% | 0
*) C_P provided here is assumed to include all WTG aerodynamic, drive train and internal electrical losses. | [6 empty] | 98815.0782 |  | 6502785.2305 | MWh/year
[7 empty] | WTG |  | Park
[6 empty] | Capacity Factor | 56.4% |  | 46.4%

## IAC
Cable 1 |  |  | 400 mm2 | 0.101 | Ohm/km
Cable 2 |  |  | 630 mm2 | 0.063 | Ohm/km
Cable 3 |  |  | 800 mm2 | 0.037 | Ohm/km
|  |  | WTG 1 | WTG 2 | WTG 3 | WTG 4
WTG Nominal Power [MVA] |  |  | 21.1 | 21.1 | 21.1 | 21.1
IAC Voltage kV |  |  | 66 | 66 | 66 | 66
# WTGs on IAC Section |  |  | 1 | 2 | 3 | 4
Nominal Current [A] on IAC Section |  |  | 184.16 | 368.32 | 552.48 | 736.64
IAC Section Cable 1 / 2 / 3 |  |  | 1 | 1 | 2 | 3
Resistance [Ohm/km] |  |  | 0.101 | 0.101 | 0.063 | 0.037
|  |  | km | km | km | km
String Section Length [km] |  |  | 2.5 | 2.5 | 2 | 1.5
Free Wind Speed | Power | [5 empty] | P_loss | hours | Loss
(m/s) | MW | MVA |  |  |  |  | [kW] |  | [MWh/year]
0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57 | 0
1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 151.986 | 0
2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 293.9856 | 0
3.5 | 0.437 | 0.46 | 0.01221 | 0.048841 | 0.054837 | 0.042941 | 0.15883 | 423.2832 | 0.06723
4.5 | 1.423 | 1.4979 | 0.12947 | 0.51788 | 0.58146 | 0.45533 | 1.6841 | 559.764 | 0.94272
5.5 | 2.83 | 2.9789 | 0.51208 | 2.0483 | 2.2998 | 1.8009 | 6.661 | 670.7532 | 4.4679
6.5 | 4.772 | 5.0232 | 1.456 | 5.824 | 6.539 | 5.1205 | 18.9396 | 764.9232 | 14.4873
7.5 | 7.46 | 7.8526 | 3.5583 | 14.2331 | 15.9805 | 12.5138 | 46.2857 | 827.6448 | 38.3081
8.5 | 10.949 | 11.5253 | 7.665 | 30.6599 | 34.424 | 26.9564 | 99.7052 | 842.6244 | 84.0141
9.5 | 14.623 | 15.3926 | 13.6721 | 54.6883 | 61.4025 | 48.0823 | 177.8451 | 799.1748 | 142.1293
10.5 | 17.73 | 18.6632 | 20.0992 | 80.3968 | 90.2673 | 70.6855 | 261.4487 | 717.6192 | 187.6206
11.5 | 19.442 | 20.4653 | 24.1681 | 96.6725 | 108.5412 | 84.9952 | 314.3771 | 620.3832 | 195.0343
12.5 | 19.921 | 20.9695 | 25.3737 | 101.4947 | 113.9554 | 89.2349 | 330.0588 | 510.27 | 168.4191
13.5 | 19.991 | 21.0432 | 25.5523 | 102.2092 | 114.7577 | 89.8632 | 332.3824 | 399.2808 | 132.7139
14.5 | 20 | 21.0526 | 25.5753 | 102.3013 | 114.8611 | 89.9441 | 332.6818 | 295.4748 | 98.2991
15.5 | 20 | 21.0526 | 25.5753 | 102.3013 | 114.8611 | 89.9441 | 332.6818 | 211.4664 | 70.351
16.5 | 20 | 21.0526 | 25.5753 | 102.3013 | 114.8611 | 89.9441 | 332.6818 | 157.7676 | 52.4864
17.5 | 20 | 21.0526 | 25.5753 | 102.3013 | 114.8611 | 89.9441 | 332.6818 | 123.954 | 41.2372
18.5 | 20 | 21.0526 | 25.5753 | 102.3013 | 114.8611 | 89.9441 | 332.6818 | 100.3896 | 33.3978
19.5 | 20 | 21.0526 | 25.5753 | 102.3013 | 114.8611 | 89.9441 | 332.6818 | 75.6864 | 25.1795
20.5 | 20 | 21.0526 | 25.5753 | 102.3013 | 114.8611 | 89.9441 | 332.6818 | 53.6112 | 17.8355
21.5 | 20 | 21.0526 | 25.5753 | 102.3013 | 114.8611 | 89.9441 | 332.6818 | 38.106 | 12.6772
22.5 | 20 | 21.0526 | 25.5753 | 102.3013 | 114.8611 | 89.9441 | 332.6818 | 25.7544 | 8.568
23.5 | 18.4 | 19.3684 | 21.647 | 86.5878 | 97.2184 | 76.1287 | 281.5819 | 15.8556 | 4.4646
24.5 | 15.2 | 16 | 14.7723 | 59.0892 | 66.3437 | 51.9517 | 192.157 | 9.5484 | 1.8348
25.5 | 12 | 12.6316 | 9.2071 | 36.8285 | 41.35 | 32.3799 | 119.7654 | 6.2196 | 0.74489
26.5 | 8.8 | 9.2632 | 4.9514 | 19.8055 | 22.2371 | 17.4132 | 64.4072 | 3.4164 | 0.22004
27.5 | 5.6 | 5.8947 | 2.0051 | 8.0204 | 9.0051 | 7.0516 | 26.0823 | 2.3652 | 0.06169
28.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
[8 empty] | 8759.308 |  | h/year
IAC String Losses (MWh/year) | [8 empty] | 1335.5623 | MWh/year
WTG Energy Yield (MWh/year) | [8 empty] | 395260.3128 | MWh/year
Losses (% WTG Energy Yield/year) | [8 empty] | 0.3379% | /year

## IAC_2
Cable 1 |  |  | 400 mm2 | 0.101 | Ohm/km
Cable 2 |  |  | 630 mm2 | 0.063 | Ohm/km
Cable 3 |  |  | 800 mm2 | 0.037 | Ohm/km
|  |  | WTG 1 | WTG 2 | WTG 3 | WTG 4
WTG Nominal Power [MVA] |  |  | 21.1 | 21.1 | 21.1 | 21.1
IAC Voltage kV |  |  | 66 | 66 | 66 | 66
# WTGs on IAC Section |  |  | 1 | 2 | 3 | 4
Nominal Current [A] on IAC Section |  |  | 92.1 | 184.2 | 276.3 | 368.4
IAC Section Cable 1 / 2 / 3 |  |  | 1 | 1 | 1 | 1
Resistance [Ohm/km] |  |  | 0.101 | 0.101 | 0.101 | 0.101
|  |  | km | km | km | km
String Section Length [km] |  |  | 2.5 | 2.5 | 2 | 1.5
Free Wind Speed | Power | [5 empty] | P_loss | hours | Loss
(m/s) | MW | MVA |  |  |  |  | [kW] |  | [MWh/year]
0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57 | 0
1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 151.986 | 0
2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 293.9856 | 0
3.5 | 0.437 | 0.46 | 0.0030539 | 0.012216 | 0.021988 | 0.029317 | 0.066575 | 423.2832 | 0.02818
4.5 | 1.423 | 1.4979 | 0.032382 | 0.12953 | 0.23315 | 0.31086 | 0.70592 | 559.764 | 0.39515
5.5 | 2.83 | 2.9789 | 0.12807 | 0.5123 | 0.92214 | 1.2295 | 2.792 | 670.7532 | 1.8728
6.5 | 4.772 | 5.0232 | 0.36416 | 1.4566 | 2.6219 | 3.4959 | 7.9387 | 764.9232 | 6.0725
7.5 | 7.46 | 7.8526 | 0.88995 | 3.5598 | 6.4077 | 8.5436 | 19.401 | 827.6448 | 16.0571
8.5 | 10.949 | 11.5253 | 1.9171 | 7.6683 | 13.8029 | 18.4039 | 41.7922 | 842.6244 | 35.2151
9.5 | 14.623 | 15.3926 | 3.4195 | 13.678 | 24.6204 | 32.8272 | 74.5451 | 799.1748 | 59.5746
10.5 | 17.73 | 18.6632 | 5.027 | 20.1079 | 36.1943 | 48.259 | 109.5882 | 717.6192 | 78.6426
11.5 | 19.442 | 20.4653 | 6.0447 | 24.1786 | 43.5215 | 58.0287 | 131.7735 | 620.3832 | 81.7501
12.5 | 19.921 | 20.9695 | 6.3462 | 25.3847 | 45.6925 | 60.9233 | 138.3466 | 510.27 | 70.5941
13.5 | 19.991 | 21.0432 | 6.3909 | 25.5634 | 46.0141 | 61.3522 | 139.3206 | 399.2808 | 55.628
14.5 | 20 | 21.0526 | 6.3966 | 25.5864 | 46.0556 | 61.4074 | 139.4461 | 295.4748 | 41.2028
15.5 | 20 | 21.0526 | 6.3966 | 25.5864 | 46.0556 | 61.4074 | 139.4461 | 211.4664 | 29.4882
16.5 | 20 | 21.0526 | 6.3966 | 25.5864 | 46.0556 | 61.4074 | 139.4461 | 157.7676 | 22.0001
17.5 | 20 | 21.0526 | 6.3966 | 25.5864 | 46.0556 | 61.4074 | 139.4461 | 123.954 | 17.2849
18.5 | 20 | 21.0526 | 6.3966 | 25.5864 | 46.0556 | 61.4074 | 139.4461 | 100.3896 | 13.9989
19.5 | 20 | 21.0526 | 6.3966 | 25.5864 | 46.0556 | 61.4074 | 139.4461 | 75.6864 | 10.5542
20.5 | 20 | 21.0526 | 6.3966 | 25.5864 | 46.0556 | 61.4074 | 139.4461 | 53.6112 | 7.4759
21.5 | 20 | 21.0526 | 6.3966 | 25.5864 | 46.0556 | 61.4074 | 139.4461 | 38.106 | 5.3137
22.5 | 20 | 21.0526 | 6.3966 | 25.5864 | 46.0556 | 61.4074 | 139.4461 | 25.7544 | 3.5913
23.5 | 18.4 | 19.3684 | 5.4141 | 21.6564 | 38.9814 | 51.9753 | 118.0271 | 15.8556 | 1.8714
24.5 | 15.2 | 16 | 3.6947 | 14.7787 | 26.6017 | 35.4689 | 80.544 | 9.5484 | 0.76907
25.5 | 12 | 12.6316 | 2.3028 | 9.2111 | 16.58 | 22.1067 | 50.2006 | 6.2196 | 0.31223
26.5 | 8.8 | 9.2632 | 1.2384 | 4.9535 | 8.9164 | 11.8885 | 26.9968 | 3.4164 | 0.092232
27.5 | 5.6 | 5.8947 | 0.50149 | 2.006 | 3.6108 | 4.8143 | 10.9326 | 2.3652 | 0.025858
28.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
[8 empty] | 8759.308 |  | h/year
IAC String Losses (MWh/year) | [8 empty] | 559.811 | MWh/year
WTG Energy Yield (MWh/year) | [8 empty] | 395260.3128 | MWh/year
Losses (% WTG Energy Yield/year) | [8 empty] | 0.1416% | /year